## DRAS
This document and its attachments, if any, contains confidential and proprietary information belonging to MIDOR, and/or other third parties, including Technip Italy S.p.A. . The intended recipient of the information contained herein shall not divulge the same to any third party or sell, trade, publish, reproduce or reverse engineer the same, in any manner, without MIDOR prior written consent and/or Technip Italy S.p.A. prior written consent, and shall not put in use the information for any purpose unrelated to that for which it has been transmitted to recipient. Any disclosure and use of the contents hereof shall be subject to any subsisting agreements between MIDOR, Technip Italy S.p.A. and the intended recipient. The copyright in this document and/or attachments is owned by MIDOR and Technip Italy S.p.A., while the underlying IP is owned by other Technology Providers and any reproduction or adaptation thereof shall require MIDOR’s and/or, when needed, Technip Italy S.p.A.'s express written approval.
[5 empty] | Document Review and Approval Sheet | [9 empty] | Status
[6 empty] | DRAS_2544-00-MR-1547-105_A | [8 empty] | Open
Closed
| MIDOR REFINERY EXPANSION PROJECT | [11 empty] | OWNER Response Status
[13 empty] | AF | Approved without comments | Contractor status
|  | OWNER Transmittal Document |  |  |  | in reply to CONTRACTOR Transmittal Document |  |  |  | Document reference |  |  | RF | Reviewed without comments | Implemented
|  | Reference | Date |  |  | Reference | TPIT-MIDOR-T-11416 |  |  | Document n° | 2544-00-MR-1547-105 |  | AC | Approved with comments | Noted, will be implemented
|  | MIDOR-TPIT-T-XXXXX |  |  |  | Date | 20/06/2019 |  |  | Rev. | A |  | RC | Reviewed with comments | No modification is necessary, clarification follows
[6 empty] | Material requisition |  |  |  | Description | MATERIAL REQUISITION FOR MAGNETIC FLOW METERS |  | NA | Not Approved | Modification is subject to Change Order Approval
|  | Response Status |  |  |  | Vendor Name |  |  |  | Issued by (Contractor Discipline) | INSTRUMENTATION AND AUTOMATION
|  | RC | Reviewed with comments
| Pos. | Tag | Document Reference (i.e. paragraph, sheet, note) | OWNER Comment |  | Contractor Reply |  |  | OWNER Counter Reply |  | Final Agreement | Status (Open/ Closed)
|  |  |  | Date | 2019-07-04 | Date | 2019-07-12 |  | Date |  | Date
|  |  |  | By | Comment | Status | Reply | int.code
| 1 | 3500 | 2544-00-SP-1547-105 | M.seif | contarctor shall follow 2544-00-JSD-1540-01-3 and 2544-00-JSD-1547-01-1 and comply with them | No modification is necessary, clarification follows | Contractor confirms
| 2 | 3501 | 2544-00-MR-1547-105 | M.seif | 2544-54-SP-1500-40 not found on MR attachments | No modification is necessary, clarification follows | Contractor will verify
| 3 | 3502 | General | M.seif | Row 1 tag number,contractor to calrify spacing in ( 54-FT -1020) it should be 54-FT-1020 | No modification is necessary, clarification follows | The tag number is created in Smart Plant according to the project procedure.
| 4 | 3503 | General | M.seif | Row 51 Requisition No. : 2544-00-MR-1547-105 shall comply with Row 52 Material Code 154705 , kindly fix it. | No modification is necessary, clarification follows | Contractor confirms that the informations are according to the project procedure. The progressive 105 in the MR requisition is for TPIT scope of supply.
| 5 | 3503 | General | M.seif | Row 1 tag Tag name to comply with P&ID which is 54-FIT-XXX | No modification is necessary, clarification follows | The tag number is created in Smart Plant according to the project procedure.
| 6 | 10001 | General | M.Gabr | Vendor shall be instructed to submit the sub vendor list for solenoid | No modification is necessary, clarification follows | Please clarify the comment
| 7 | 10002 | General | M.Gabr | There is no mention for the required guarantee | No modification is necessary, clarification follows | Warranty will in accordance with contractor requirements.
| 8 | 10003 | General | M.GABR | TO VERIFY THAT THE REQUIRED ITEMS ARE IDENTICAL TO THE ITEMS WHICH WERE REQUIRED IN EW PHASE | No modification is necessary, clarification follows | The items included in the MR are only for the interconnecting area according to the schedule of the 1st PO.
| 9 | 10004 | General | M.GABR | The actioned procedures that will followed to be submitted in case the vendor proposed alternative or design modifictation different from the required origin sepecfication | No modification is necessary, clarification follows | Please clarify the comment
| 10 | 10005 | 2544-00-SR-1547-105 | M.GABR | Although it is mentioned in Part II page 4/5- A5008 that vendor to submit a list of special tools, it is not mentioned in Part I page 3-5 additional material and services Please clarify. | No modification is necessary, clarification follows
| 11 | 22001 | 2544-54-SP-1547-105 | E. Gallardo | Please include the Line size, Pipe Material, Pipe schedule in Data Sheet (Item 7, 8) not as a note. | Noted, will be implemented | The data will be included automatically when all the information about the line ( material, fluid, schedule ) will be imported in the data base.
| 12 | 22002 | 2544-54-SP-1547-105 | E. Gallardo | For Liner material (Item 27) please include Teflon as min / VTA (Vendor To Advised). | Noted, will be implemented
| 13 | 22003 | 2544-54-SP-1547-105 | E. Gallardo | Include Minimum Fluid Conductivity (Item 20). Could be indicate as min that shall be > =10 µs/cm. | Noted, will be implemented
| 14 | 22004 | 2544-54-SP-1547-105 | E. Gallardo | Area Classification (Item 36) include the reference of "Note 2" | Noted, will be implemented
| 15 | 22005 | 2544-54-SP-1547-105 | E. Gallardo | Include Transmitter Enclosure material. | No modification is necessary, clarification follows | The information will be included after Vendor selection
| 16 | 22006 | 2544-54-SP-1547-105 | E. Gallardo | Include the following Notes: Flowmeter shall be supply totally assembled (electronics and sensor), including cable and accessories. All instruments shall be identified (Tag Name) with a SS plate permantly attached to body. Flow meter shall be supply calibrated from factory, vendor shall provide the calibration certificate. | Noted, will be implemented
| 17 | 22007 | 2544-54-SP-1547-105 | E. Gallardo | Electrode Type: 2 Electrodes + ground Grounding Type: Ground rings 316L SS (Note: if more than one ground ring is to be used as per service conditions VTA). | No modification is necessary, clarification follows | The informations are according to the project specification. After Vendor selection the data will be update.
| 18 | 22008 | 2544-54-SP-1547-105 | E. Gallardo | Please include the Velocity Range or the velocity values for flow min/oper/max. Include the Repeatability and response time required. Include Calibration Range for transmitter and eng. Units (e.g m3/h). Please include that the transmitter will be supply with LCD display ( for integral flow indicator). | Noted, will be implemented | Repeatability 0,1 % or better
| 19 | 22009 | 2544-54-SP-1547-105 | E. Gallardo | Regarding Mounting Kit (Item 44), please consider to include in the vendor supply the grounding cable with accessories, provide the cable length meters to be consider by vendor. | No modification is necessary, clarification follows | The cables will be included in the MR 1574-101
| 20 | 22010 | 2544-00-SR-1547-105 | E. Gallardo | Please confirm if this SR includes the total of Magnetic Flowmeters for the entaire project or will be included other units. | No modification is necessary, clarification follows | Contractor confirms that the MR includes only the instrument of the unit 53 for the 1st PO according to the schedule
| 21 | 29001 | 2544-00-MR-1547-105 | E. Perez | The following specs do not apply: 2544-00-JSS-6300-02 & 2544-00-JSS-6300-05 | Noted, will be implemented
| 22 | 29002 | 2544-00-ITP-1547-105 (Page 2/2 - Before fab stage) | E. Perez | Add in activities: WPS and PQR (R) | Noted, will be implemented
| 23 | 29002 | 2544-00-ITP-1547-105 (Page 2/2 - During fab stage) | E. Perez | Reference for PMI is incomplete, being the correct one 2544-00-JSS-6300-04. | Noted, will be implemented
| 24 | 29004 | 2544-00-ITP-1547-105 (Page 2/2 - During fab stage) | E. Perez | Please, clarify the criterion chosen for NDE (MP/LP for items rating up to 600# and Rx+MP/LP for 900# an above) | No modification is necessary, clarification follows | The criteria must be discussed with the Inspection section.

## Sheet1
INSTRUCTION FOR COMMENTING DOCUMENTS
1 | There is ONE Comment sheet for each DOCUMENT.
2 | All the comments during document approval life cycles should be registered in it`s comment sheet
3 | Commenting format on document should be Text Box Tool, Arial, 11.
4 | Original documents will have comment numbers only while comment sheet should contain comment numbers and appropriate comments
5 | While numbering comments, make sure Table 1 is applied
6 | In case of deletion of comment (number X ) before sending to Contractor, comment number for this deletion will stay and next comment will be numbered as X+1
7 | Document Owner (Discipline) should incorporate all comments received from other disciplines and make unique comment sheet
Table 1 - Comment Numbering allocation
| MIDOR |  | Comment Numbering allocation
| Disciplines |  | Start | Finish
| Process |  | `0001 | 1000
| Mechanical |  | 1001 | 2000
| Electrical |  | 2001 | 3000
| Instrumentation |  | 3001 | 4000
| Civil |  | 4001 | 5000
| HSE |  | 5001 | 6000
| COMM-OPS |  | 6001 | 7000
| QA\QC |  | 7001 | 8000
| Construction |  | 8001 | 9000
| Project Controls |  | 9001 | 10000
| Procurement |  | 10001 | 11000
| Contracts |  | 11001 | 12000
| Interface Management |  | 12001 | 13000
| Directorate |  | 13001 | 14000
| Site Management |  | 14001 | 15000
| Legal |  | 15001 | 16000
| Laboratory |  | 16001 | 17000
| Project Management |  | 17001 | 18000
PMC
| PMC Process |  | 18001 | 20000
| PMC Mechanical (Rotating) |  | 20001 | 20300
| PMC Technology |  | 20301 | 20600
| PMC Vessels & H.Exchangers Engineer |  | 20601 | 21000
| PMC Piping |  | 21001 | 21500
| PMC Electrical |  | 21501 | 22000
| PMC Instrumentation |  | 22001 | 23000
| PMC Civil |  | 23001 | 24000
| PMC HSE |  | 24001 | 25000
| PMC COMM-OPS |  | 25001 | 26000
| PMC QA\QC |  | 26001 | 27000
| PMC Construction |  | 27001 | 28000
| PMC Project Controls |  | 28001 | 29000
| PMC Procurement |  | 29001 | 30000
| PMC Contracts |  | 30001 | 31000
| PMC Interface Management |  | 31001 | 32000
| PMC Site Management |  | 32001 | 33000
| PMC Legal |  | 33001 | 34000
| PMC Laboratory |  | 34001 | 35000
| PMC Project Management |  | 35001 | 36000